E-MON

E-Mon D-Mon BACnet, ModBus, and LonWorks Point Maps

CL3200, CL3400, CL5000 and IDR

6/21/2012

Contents

ModBus Point Map: Class 3200, 3400, and 5000 Meters	3

ModBus Point Map: Legacy Class 3000 and 5000 Meters	5

ModBus Point Map: IDR8 and IDR16	6

ModBus Point Map: Legacy IDR	8

BACnet Object Descriptors: Class 3200, 3400, and 5000 Meters	9

BACnet Object Descriptors: Legacy Class 3000 and 5000 Meters	11

BACnet Object Descriptors: IDR8 and IDR16	12

BACnet Object Descriptors: Legacy IDR	14

LonWorks Pointmap: Class 3400 and 5000 Meters	15

LonWorks Pointmap: Legacy Class 3000 and 5000 Meters	16

LonWorks Pointmap: IDR8 and IDR16	17

LonWorks Pointmap: Legacy IDR	19

PIC STATEMENT for Class 3200, 3400, 5000 Meters & IDRs	20

E-Mon D-Mon ModBus Point Map: Class 3200, 3400, and 5000 Meters

| Address | Registers | Format | Description | Units | CL3200 | CL3400/CL5000 | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 40001 | 2 | Integer | Energy delivered | Wh Pulse | R/W | R/W | 1 |
| 40003 | 2 | Integer | Energy received | Wh Pulse | R/W | R/W | 1 |
| 40005 | 2 | Integer | Reactive energy delivered | VARh Pulse | R/W | R/W | 1 |
| 40007 | 2 | Integer | Reactive energy received | VARh Pulse | R/W | R/W | 1 |
| 41001 | 2 | Float | Energy delivered | kWh | R/W | R/W | 1 |
| 41003 | 2 | Float | Energy received | kWh | R/W | R/W | 1 |
| 41005 | 2 | Float | Reactive energy delivered | kVARh | R/W | R/W | 1 |
| 41007 | 2 | Float | Reactive energy received | kVARh | R/W | R/W | 1 |
| 41009 | 2 | Float | Real power | kW | R | R |  |
| 41011 | 2 | Float | Reactive power | kVAR | R | R |  |
| 41013 | 2 | Float | Apparent power | kVA | R | R |  |
| 41015 | 2 | Float | Power factor | % PF | R | R |  |
| 41017 | 2 | Float | Peak demand | kW | R | R |  |
| 41019 | 2 | Float | Current average | Amps | R | R |  |
| 41021 | 2 | Float | Voltage line-neutral | Volts-N | R | R |  |
| 41023 | 2 | Float | Voltage line-line | Volts-L | R | R |  |
| 41025 | 2 | Float | Frequency | Hz | R | R |  |
| 41027 | 2 | Float | Phase angle | Degree | R | R |  |
| 41029 | 2 | Float | Real power, phase A | kW | R | R |  |
| 41031 | 2 | Float | Real power, phase B | kW | R | R |  |
| 41033 | 2 | Float | Real power, phase C | kW | R | R |  |
| 41035 | 2 | Float | Reactive power, phase A | kVAR | R | R |  |
| 41037 | 2 | Float | Reactive power, phase B | kVAR | R | R |  |
| 41039 | 2 | Float | Reactive power, phase C | kVAR | R | R |  |
| 41041 | 2 | Float | Apparent power, phase A | kVA | R | R |  |
| 41043 | 2 | Float | Apparent power, phase B | kVA | R | R |  |
| 41045 | 2 | Float | Apparent power, phase C | kVA | R | R |  |
| 41047 | 2 | Float | Power factor, phase A | % PF | R | R |  |
| 41049 | 2 | Float | Power factor, phase B | % PF | R | R |  |
| 41051 | 2 | Float | Power factor, phase C | % PF | R | R |  |
| 41053 | 2 | Float | Current, phase A | Amps | R | R |  |
| 41055 | 2 | Float | Current, phase B | Amps | R | R |  |
| 41057 | 2 | Float | Current, phase C | Amps | R | R |  |
| 41059 | 2 | Float | Voltage, line to neutral, phase A-N | Volts-N | R | R |  |
| 41061 | 2 | Float | Voltage, line to neutral, phase B-N | Volts-N | R | R |  |
| 41063 | 2 | Float | Voltage, line to neutral, phase C-N | Volts-N | R | R |  |
| 41065 | 2 | Float | Voltage, line to line, phase A-B | Volts-L | R | R |  |
| 41067 | 2 | Float | Voltage, line to line, phase B-C | Volts-L | R | R |  |
| 41069 | 2 | Float | Voltage, line to line, phase C-A | Volts-L | R | R |  |
| 41071 | 2 | Float | Phase angle, phase A | Degree | R | R |  |
| 41073 | 2 | Float | Phase angle, phase B | Degree | R | R |  |
| 41075 | 2 | Float | Phase angle, phase C | Degree | R | R |  |
| 41083 | 2 | Float | External Input 1 | Pulse |  | R/W | 2 |
| 41085 | 2 | Float | External Input 2 | Pulse |  | R/W | 2 |
| 44001 | 6 | Custom | Interval Day Block |  | R/W | R/W | 3 |
| 44007 | 1 per interval | Integer | Interval Data | Pulse | R | R | 4 |
| 45501 | 2 per day | Custom | Interval Data Headers |  | R | R | 5 |
| 46025 | 8 | Custom | RTC Date/Time |  | R/W | R/W | 6 |
| 46049 | 8 | Custom | EZ7 ID, ModBus ID, Serial Number |  | R/W | R/W | 7 |
| 46057 | 8 | Custom | Recorder Info., Demand Interval |  | R/W | R/W |  |
| 46513 | 8 | Custom | Flags L1: Power Failure, Battery |  | R | R |  |
| 46521 | 8 | Custom | Flags L2: Power Failure Date |  | R | R |  |

- To clear single meter kWh/kVARh, set multiple points at 40001 or 41001 for 8 points with data set to 0000 0000 0000 0000 0000 0000 0000 0000.

Jumper J6 must be closed.

- External inputs are standard on Class 5000 meters and optional on Class 3400 meters (Part of Expanded Feature Package).

To clear external inputs, set multiple points at 41083 or 41085 for 2 points with data set to 0000 0000.  Jumper J6 must be closed.

- To set the interval data day block, set multiple points at 44001 for 6 points with data set to 0C0I 0000 MMDD YYYY 0000 0000.

0C = Channel, 0I = Interval (0F = 15 minute intervals, 05 = 5 minute intervals)

- Each register represents a 15 or 5 minute kWh pulse value based on the interval day block.  96 registers max with 15 minute intervals.  288 registers max with 5 minute intervals.  The first interval data register 44007 represents the pulse count for the first 15 or 5 minute interval beginning at midnight.

- The interval data headers represent days with available interval data.  Each day represents 2 registers.  Format: MMDD YYYY.

- To set the date and time, set multiple points at 46025 for 4 points with data set to HHMM SSDW MMDD YYYY (DW=day of week)

- To change the ModBus ID, set single point at 46050 with data set to new ModBus ID (e.g. 1 to 247).  Jumper J6 must be closed.

- E-Mon D-Mon ModBus Point Map: Legacy Class 3000 and 5000 Meters

| Address | Registers | Format | Description | Units | Legacy CL3000 CL5000 RTU | LegacyCL3000 CL5000 TCP/IP | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 40001 | 2 | Integer | Energy delivered | Wh Pulse | R/W | R | 1 |
| 40003 | 2 | Integer | Energy received | Wh Pulse | R/W | R | 1 |
| 40005 | 2 | Integer | Reactive energy delivered | VARh Pulse | R/W | R | 1 |
| 40007 | 2 | Integer | Reactive energy received | VARh Pulse | R/W | R | 1 |
| 41001 | 2 | Float | Energy delivered | kWh | R/W | R | 2 |
| 41003 | 2 | Float | Energy received | kWh | R/W | R | 2 |
| 41005 | 2 | Float | Reactive energy delivered | kVARh | R/W | R | 2 |
| 41007 | 2 | Float | Reactive energy received | kVARh | R/W | R | 2 |
| 41009 | 2 | Float | Real power | kW | R | R |  |
| 41011 | 2 | Float | Reactive power | kVAR | R | R |  |
| 41013 | 2 | Float | Apparent power | kVA | R | R |  |
| 41015 | 2 | Float | Power factor | % PF | R | R |  |
| 41017 | 2 | Float | Current total | Amps | R | R |  |
| 41019 | 2 | Float | Current average | Amps | R | R |  |
| 41021 | 2 | Float | Voltage line-neutral | Volts-N | R | R |  |
| 41023 | 2 | Float | Voltage line-line | Volts-L | R | R |  |
| 41025 | 2 | Float | Frequency | Hz | R | R |  |
| 41027 | 2 | Float | Phase angle | Degree | R | R |  |
| 41029 | 2 | Float | Real power, phase A | kW | R | R |  |
| 41031 | 2 | Float | Real power, phase B | kW | R | R |  |
| 41033 | 2 | Float | Real power, phase C | kW | R | R |  |
| 41035 | 2 | Float | Reactive power, phase A | kVAR | R | R |  |
| 41037 | 2 | Float | Reactive power, phase B | kVAR | R | R |  |
| 41039 | 2 | Float | Reactive power, phase C | kVAR | R | R |  |
| 41041 | 2 | Float | Apparent power, phase A | kVA | R | R |  |
| 41043 | 2 | Float | Apparent power, phase B | kVA | R | R |  |
| 41045 | 2 | Float | Apparent power, phase C | kVA | R | R |  |
| 41047 | 2 | Float | Power factor, phase A | % PF | R | R |  |
| 41049 | 2 | Float | Power factor, phase B | % PF | R | R |  |
| 41051 | 2 | Float | Power factor, phase C | % PF | R | R |  |
| 41053 | 2 | Float | Current, phase A | Amps | R | R |  |
| 41055 | 2 | Float | Current, phase B | Amps | R | R |  |
| 41057 | 2 | Float | Current, phase C | Amps | R | R |  |
| 41059 | 2 | Float | Voltage, line to neutral, phase A-N | Volts-N | R | R |  |
| 41061 | 2 | Float | Voltage, line to neutral, phase B-N | Volts-N | R | R |  |
| 41063 | 2 | Float | Voltage, line to neutral, phase C-N | Volts-N | R | R |  |
| 41065 | 2 | Float | Voltage, line to line, phase A-B | Volts-L | R | R |  |
| 41067 | 2 | Float | Voltage, line to line, phase B-C | Volts-L | R | R |  |
| 41069 | 2 | Float | Voltage, line to line, phase C-A | Volts-L | R | R |  |
| 41071 | 2 | Float | Phase angle, phase A | Degree | R | R |  |
| 41073 | 2 | Float | Phase angle, phase B | Degree | R | R |  |
| 41075 | 2 | Float | Phase angle, phase C | Degree | R | R |  |
| 41077 | 2 | Float | Reserve A | No units | R | R |  |
| 41079 | 2 | Float | Reserve B | No units | R | R |  |
| 41081 | 2 | Float | Reserve C | No units | R | R |  |
| 41083 | 2 | Float | External Input 1 | Pulse | R/W | R | 3 |
| 41085 | 2 | Float | External Input 2 | Pulse | R/W | R | 3 |
| 46025 | 8 | Custom | RTC Date/Time |  | R/W | R/W | 4 |
| 46049 | 8 | Custom | EZ7 ID, ModBus ID, Serial Number |  | R/W | R/W | 5 |
| 46513 | 8 | Custom | Flags L1: Power Failure, Battery |  | R | R |  |
| 46521 | 8 | Custom | Flags L2: Power Failure Date |  | R | R |  |

- To clear single register, set single register (ex. 40001) with data set to 0000.  Jumper J2 must be closed.  Can only clear using ModBus RTU.

- To clear single register, set single register (ex. 41001) with data set to 0000.  Jumper J2 must be closed.  Can only clear using ModBus RTU.

- External inputs are not available on Class 3200 meters.  To clear external inputs, set single point at register 41083 or 41085 with data set to 0000. Jumper J2 must be closed.  Can only clear using ModBus RTU.  Protocessor module must be removed to access ModBus RTU.

- To set the date and time, set multiple points at 46025 for 4 points with data set to HHMM SSDW MMDD YYYY (DW=day of week)

- To change the ModBus ID, set single point at 46049 with data set to new ModBus ID (e.g. 1 to 247).  Jumper J2 must be closed.

E-Mon D-Mon ModBus Point Map: IDR8 and IDR16

| Integer Address | Float Address | Registers | Description | Integer Units | Float Units | IDR | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 40001 | 41001 | 2 | Usage Channel 1 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40003 | 41003 | 2 | Usage Channel 2 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40005 | 41005 | 2 | Usage Channel 3 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40007 | 41007 | 2 | Usage Channel 4 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40009 | 41009 | 2 | Usage Channel 5 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40011 | 41011 | 2 | Usage Channel 6 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40013 | 41013 | 2 | Usage Channel 7 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40015 | 41015 | 2 | Usage Channel 8 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40017 | 41017 | 2 | Usage Channel 9 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40019 | 41019 | 2 | Usage Channel 10 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40021 | 41021 | 2 | Usage Channel 11 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40023 | 41023 | 2 | Usage Channel 12 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40025 | 41025 | 2 | Usage Channel 13 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40027 | 41027 | 2 | Usage Channel 14 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40029 | 41029 | 2 | Usage Channel 15 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40031 | 41031 | 2 | Usage Channel 16 | Pulse | Pulse * Pulse Value | R/W | 1 |
| 40065 | 41065 | 2 | Demand Channel 1 | Demand | Demand * Pulse Value | R |  |
| 40067 | 41067 | 2 | Demand Channel 2 | Demand | Demand * Pulse Value | R |  |
| 40069 | 41069 | 2 | Demand Channel 3 | Demand | Demand * Pulse Value | R |  |
| 40071 | 41071 | 2 | Demand Channel 4 | Demand | Demand * Pulse Value | R |  |
| 40073 | 41073 | 2 | Demand Channel 5 | Demand | Demand * Pulse Value | R |  |
| 40075 | 41075 | 2 | Demand Channel 6 | Demand | Demand * Pulse Value | R |  |
| 40077 | 41077 | 2 | Demand Channel 7 | Demand | Demand * Pulse Value | R |  |
| 40079 | 41079 | 2 | Demand Channel 8 | Demand | Demand * Pulse Value | R |  |
| 40081 | 41081 | 2 | Demand Channel 9 | Demand | Demand * Pulse Value | R |  |
| 40083 | 41083 | 2 | Demand Channel 10 | Demand | Demand * Pulse Value | R |  |
| 40085 | 41085 | 2 | Demand Channel 11 | Demand | Demand * Pulse Value | R |  |
| 40087 | 41087 | 2 | Demand Channel 12 | Demand | Demand * Pulse Value | R |  |
| 40089 | 41089 | 2 | Demand Channel 13 | Demand | Demand * Pulse Value | R |  |
| 40091 | 41091 | 2 | Demand Channel 14 | Demand | Demand * Pulse Value | R |  |
| 40093 | 41093 | 2 | Demand Channel 15 | Demand | Demand * Pulse Value | R |  |
| 40095 | 41095 | 2 | Demand Channel 16 | Demand | Demand * Pulse Value | R |  |

- To clear a single channel register, set multiple points at desired register (ex. 40001 or 41001) for 2 points with data set to 0000 0000.  Jumper J6 must be closed.

| Address | Registers | Format | Description |  | IDR | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| 44001 | 6 | Custom | Interval Day Block |  | R/W | 1 |
| 44007 | 1 per interval | Integer | Interval Data |  | R | 2 |
| 45501 | 2 per day | Custom | Interval Data Headers |  | R | 3 |
| 46025 | 8 | Custom | RTC Date/Time |  | R/W | 4 |
| 46049 | 8 | Custom | EZ7 ID, ModBus ID, Serial Number |  | R/W | 5 |
| 46057 | 8 | Custom | Recorder Info., Demand Interval |  | R/W |  |
| 46513 | 8 | Custom | Flags L1: Power Failure, Battery |  | R |  |
| 46521 | 8 | Custom | Flags L2: Power Failure Date |  | R |  |

- To set the interval data day block, set multiple points at 44001 for 6 points with data set to 0C0I 0000 MMDD YYYY 0000 0000.

0C = Channel, 0I = Interval (0F = 15 minute intervals, 05 = 5 minute intervals)

- Each register represents a 15 or 5 minute pulse value based on the interval day block.  96 registers max with 15 minute intervals.  288 registers max with 5 minute intervals.  The first interval data register 44007 represents the pulse count for the first 15 or 5 minute interval beginning at midnight.

- The interval data headers represent days with available interval data.  Each day represents 2 registers.  Format: MMDD YYYY.

- To set the date and time, set multiple points at 46025 for 4 points with data set to HHMM SSDW MMDD YYYY (DW=day of week)

- To change the ModBus ID, set single point at 46050 with data set to new ModBus ID (e.g. 1 to 247).  Jumper J6 must be closed.

With an IDR16 each channel 1 through 16 represents the IDR16 meter jack inputs 1 through 16.

With an IDR8 each channel 1 through 8 represents the IDR8 meter jack inputs 1 through 8.

Units are pulse counts.  The pulse value guide in Table 1 below represents the kilowatt-hour value of the meter size (amperage) plugged into the IDR meter jack.  To calculate kWh Usage and kW Demand take the number of pulses multiplied by the meter pulse value to determine total kWh and kW.  Set the EMS/BMS front end to multiply the pulse values by the pulse counts. See Table 1 below for the different meter sizes (Amperage) Watt Hour pulse values.

| Table 1 E-Mon Class 1000 & 2000 Meter Size Pulse Value Guide |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 25 Amp | 50 Amp | 100 Amp | 200 Amp | 400 Amp | 800 Amp | 1600 Amp | 3200 Amp |
| Base Watt Hour Value per Pulse for legacy E-Mon meters* (serial numbers starting with 1203XXXX and earlier) |  |  |  |  |  |  |  |
| 7.8125 | 15.625 | 31.25 | 62.50 | 125.00 | 250.00 | 500.00 | 1000.00 |
| Base Watt Hour Value per Pulse* (serial numbers above 1203XXXX) |  |  |  |  |  |  |  |
| 0.48828 | 0.97656 | 1.95313 | 3.90625 | 7.8125 | 15.625 | 31.25 | 62.50 |

*E-Mon meters support paralleling of 3 sets of up to current sensors; the Multipliers listed in Table 1 are based on 1 set of current sensors. When multiple sets of current sensors are installed in parallel, the final multiplier will be the product of the base multiplier listed in Table 1 times the number of sets of current sensors in parallel. If the meter is using more than 1 set of current sensors, be sure to also factor the number of sets into the Pulse Value.

Formula for calculating Multiplier = Base Multiplier multiplied by the number of sets of Current Sensors in Parallel.

Example: Calculate the Multiplier for a meter of 120/208 Volt, 3-Phase, 200 Amp, 3 sets of Current Sensors in parallel for a legacy meter.

The final Multiplier is 187.50 which is the result of 62.50 multiplied by 3.  The final Pulse Value is 187.50 Watt Hours per pulse.

Example: Calculate the Multiplier for a meter of 120/208 Volt, 3-Phase, 200 Amp, 3 sets of Current Sensors in parallel for a non legacy meter.

The final Multiplier is 11.71875 which is the result of 3.90625 multiplied by 3.  The final Pulse Value is 11.71875 Watt Hours per pulse.

E-Mon D-Mon ModBus Point Map: Legacy IDR

| Integer Address | Float Address | Integer Registers | Float Registers | Description | Units | RTU | TCP/IP | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 40001 | 41001 | 2 | 2 | Usage Channel 1 | Pulse | R/W | R | 1 |
| 40003 | 41003 | 2 | 2 | Usage Channel 2 | Pulse | R/W | R | 1 |
| 40005 | 41005 | 2 | 2 | Usage Channel 3 | Pulse | R/W | R | 1 |
| 40007 | 41007 | 2 | 2 | Usage Channel 4 | Pulse | R/W | R | 1 |
| 40009 | 41009 | 2 | 2 | Usage Channel 5 | Pulse | R/W | R | 1 |
| 40011 | 41011 | 2 | 2 | Usage Channel 6 | Pulse | R/W | R | 1 |
| 40013 | 41013 | 2 | 2 | Usage Channel 7 | Pulse | R/W | R | 1 |
| 40015 | 41015 | 2 | 2 | Usage Channel 8 | Pulse | R/W | R | 1 |
| 40017 | 41017 | 2 | 2 | Usage Channel 9 | Pulse | R/W | R | 1 |
| 40019 | 41019 | 2 | 2 | Usage Channel 10 | Pulse | R/W | R | 1 |
| 40021 | 41021 | 2 | 2 | Usage Channel 11 | Pulse | R/W | R | 1 |
| 40023 | 41023 | 2 | 2 | Usage Channel 12 | Pulse | R/W | R | 1 |
| 40025 | 41025 | 2 | 2 | Usage Channel 13 | Pulse | R/W | R | 1 |
| 40027 | 41027 | 2 | 2 | Usage Channel 14 | Pulse | R/W | R | 1 |
| 40029 | 41029 | 2 | 2 | Usage Channel 15 | Pulse | R/W | R | 1 |
| 40031 | 41031 | 2 | 2 | Usage Channel 16 | Pulse | R/W | R | 1 |
| 40065 | 41065 | 1 | 2 | Demand Channel 1 | Peak Demand | R/W | R/W | 2 |
| 40066 | 41067 | 1 | 2 | Demand Channel 2 | Peak Demand | R/W | R/W | 2 |
| 40067 | 41069 | 1 | 2 | Demand Channel 3 | Peak Demand | R/W | R/W | 2 |
| 40068 | 41071 | 1 | 2 | Demand Channel 4 | Peak Demand | R/W | R/W | 2 |
| 40069 | 41073 | 1 | 2 | Demand Channel 5 | Peak Demand | R/W | R/W | 2 |
| 40070 | 41075 | 1 | 2 | Demand Channel 6 | Peak Demand | R/W | R/W | 2 |
| 40071 | 41077 | 1 | 2 | Demand Channel 7 | Peak Demand | R/W | R/W | 2 |
| 40072 | 41079 | 1 | 2 | Demand Channel 8 | Peak Demand | R/W | R/W | 2 |
| 40073 | 41081 | 1 | 2 | Demand Channel 9 | Peak Demand | R/W | R/W | 2 |
| 40074 | 41083 | 1 | 2 | Demand Channel 10 | Peak Demand | R/W | R/W | 2 |
| 40075 | 41085 | 1 | 2 | Demand Channel 11 | Peak Demand | R/W | R/W | 2 |
| 40076 | 41087 | 1 | 2 | Demand Channel 12 | Peak Demand | R/W | R/W | 2 |
| 40077 | 41089 | 1 | 2 | Demand Channel 13 | Peak Demand | R/W | R/W | 2 |
| 40078 | 41091 | 1 | 2 | Demand Channel 14 | Peak Demand | R/W | R/W | 2 |
| 40079 | 41093 | 1 | 2 | Demand Channel 15 | Peak Demand | R/W | R/W | 2 |
| 40080 | 41095 | 1 | 2 | Demand Channel 16 | Peak Demand | R/W | R/W | 2 |
| 46001 | 8 | Custom | Custom | Firmware: Version, Date |  | R | R |  |
| 46009 | 8 | Custom | Custom | Device Description |  | R | R |  |
| 46025 | 8 | Custom | Custom | RTC Date/Time |  | R/W | R/W | 3 |
| 46041 | 8 | Custom | Custom | Group, Location |  | R/W | R/W |  |
| 46049 | 8 | Custom | Custom | EZ7 ID, ModBus ID |  | R/W | R | 4 |

- To clear a single integer or float usage channel register, set single point at desired register (ex. 40001 or 41001) with data set to 0000.  Jumper J7 must be closed.  Can only reset using ModBus RTU.

- To clear a single integer or float demand channel register, set single point at desired register (ex. 40065) with data set to 0000.  Jumper J7 must be closed.

- To set the date and time, set multiple points at 46025 for 4 points with data set to HHMM SSDW MMDD YYYY (DW=day of week).

- To change the ModBus ID, set single point at 46049 with data set to new ModBus ID (e.g. 1 to 247).   Can only change ModBus ID using ModBus RTU. Jumper J7 must be closed.

E-Mon D-Mon BACnet Object Descriptors: Class 3200, 3400, and 5000 Meters

| Instance ID | BACnet Object | Description | Units | BACnet Property | CL3200 | CL3400 CL5000 | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Analog Input | Energy delivered | kWh | Present Value | R | R | 1 |
| 2 | Analog Input | Energy received | kWh | Present Value | R | R | 1 |
| 3 | Analog Input | Reactive energy delivered | kVARh | Present Value | R | R | 1 |
| 4 | Analog Input | Reactive energy received | kVARh | Present Value | R | R | 1 |
| 5 | Analog Input | Real power | kW | Present Value | R | R |  |
| 6 | Analog Input | Reactive power | kVAR | Present Value | R | R |  |
| 7 | Analog Input | Apparent power | kVA | Present Value | R | R |  |
| 8 | Analog Input | Power factor | % PF | Present Value | R | R |  |
| 9 | Analog Input | Peak demand | kW | Present Value | R | R |  |
| 10 | Analog Input | Current average | Amps | Present Value | R | R |  |
| 11 | Analog Input | Voltage line-neutral | Volts-N | Present Value | R | R |  |
| 12 | Analog Input | Voltage line-line | Volts-L | Present Value | R | R |  |
| 13 | Analog Input | Frequency | Hz | Present Value | R | R |  |
| 14 | Analog Input | Phase angle | Degree | Present Value | R | R |  |
| 15 | Analog Input | Real power phase A | kW | Present Value | R | R |  |
| 16 | Analog Input | Real power phase B | kW | Present Value | R | R |  |
| 17 | Analog Input | Real power phase C | kW | Present Value | R | R |  |
| 18 | Analog Input | Reactive power phase A | kVAR | Present Value | R | R |  |
| 19 | Analog Input | Reactive power phase B | kVAR | Present Value | R | R |  |
| 20 | Analog Input | Reactive power phase C | kVAR | Present Value | R | R |  |
| 21 | Analog Input | Apparent power phase A | kVA | Present Value | R | R |  |
| 22 | Analog Input | Apparent power phase B | kVA | Present Value | R | R |  |
| 23 | Analog Input | Apparent power phase C | kVA | Present Value | R | R |  |
| 24 | Analog Input | Power factor phase A | % PF | Present Value | R | R |  |
| 25 | Analog Input | Power factor phase B | % PF | Present Value | R | R |  |
| 26 | Analog Input | Power factor phase C | % PF | Present Value | R | R |  |
| 27 | Analog Input | Current phase A | Amps | Present Value | R | R |  |
| 28 | Analog Input | Current phase B | Amps | Present Value | R | R |  |
| 29 | Analog Input | Current phase C | Amps | Present Value | R | R |  |
| 30 | Analog Input | Voltage line-neutral phase A-N | Volts-N | Present Value | R | R |  |
| 31 | Analog Input | Voltage line-neutral phase B-N | Volts-N | Present Value | R | R |  |
| 32 | Analog Input | Voltage line-neutral phase C-N | Volts-N | Present Value | R | R |  |
| 33 | Analog Input | Voltage line-line phase A-B | Volts-L | Present Value | R | R |  |
| 34 | Analog Input | Voltage line-line phase B-C | Volts-L | Present Value | R | R |  |
| 35 | Analog Input | Voltage line-line phase C-A | Volts-L | Present Value | R | R |  |
| 36 | Analog Input | Phase angle phase A | Degree | Present Value | R | R |  |
| 37 | Analog Input | Phase angle phase B | Degree | Present Value | R | R |  |
| 38 | Analog Input | Phase angle phase C | Degree | Present Value | R | R |  |
| 39 | Analog Input | Reserve A | No units | Present Value | R | R |  |
| 40 | Analog Input | Reserve B | No units | Present Value | R | R |  |
| 41 | Analog Input | Reserve C | No units | Present Value | R | R |  |
| 42 | Analog Input | External Input 1 | Pulse | Present Value |  | R | 2 |
| 43 | Analog Input | External Input 2 | Pulse | Present Value |  | R | 2 |

- To clear single meter kWh/kVARh, select reset kW/kWh on the display menu of the meter.  This function will also reset external inputs.  Jumper J6 must be closed.

- External inputs are standard on Class 5000 meters and optional on Class 3400 meters (Part of Expanded Feature Package).  To clear external inputs, select reset kW/kWh on the display menu of the meter.  This function will also reset kW/kVARh.  Jumper J6 must be closed.

| Instance ID | BACnet Object | BACnet Property | CL3200 | CL3400 CL5000 | Notes |
| --- | --- | --- | --- | --- | --- |
| BACnet Device ID | Device | Object identifier | R | R |  |
| BACnet Device ID | Device | Object name | R | R |  |
| BACnet Device ID | Device | Object type | R | R |  |
| BACnet Device ID | Device | System status | R/W | R/W |  |
| BACnet Device ID | Device | Vendor name | R | R |  |
| BACnet Device ID | Device | Vendor Identifier | R | R |  |
| BACnet Device ID | Device | Model name | R | R |  |
| BACnet Device ID | Device | Firmware revision | R | R |  |
| BACnet Device ID | Device | Application software version | R | R |  |
| BACnet Device ID | Device | Location | R/W | R/W |  |
| BACnet Device ID | Device | Description | R/W | R/W |  |
| BACnet Device ID | Device | Protocol version | R | R |  |
| BACnet Device ID | Device | Protocol services supported | R | R |  |
| BACnet Device ID | Device | Protocol object types supported | R | R |  |
| BACnet Device ID | Device | Protocol revision | R | R |  |
| BACnet Device ID | Device | Object list | R | R |  |
| BACnet Device ID | Device | Max APDU length supported | R | R |  |
| BACnet Device ID | Device | Segmentation supported | R | R |  |
| BACnet Device ID | Device | Local time | R | R |  |
| BACnet Device ID | Device | Local date | R | R |  |
| BACnet Device ID | Device | APDU timeout | R/W | R/W |  |
| BACnet Device ID | Device | Number of APDU retries | R/W | R/W |  |
| BACnet Device ID | Device | Device address binding | R | R |  |

- E-Mon D-Mon BACnet Object Descriptors: Legacy Class 3000 and 5000 Meters

| Instance ID | BACnet Object | Description | Units | BACnet Property | LegacyCL3000 | Legacy CL5000 | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Analog Input | Energy delivered | kWh | Present Value | R | R | 1 |
| 2 | Analog Input | Energy received | kWh | Present Value | R | R | 1 |
| 3 | Analog Input | Reactive energy delivered | kVARh | Present Value | R | R | 1 |
| 4 | Analog Input | Reactive energy received | kVARh | Present Value | R | R | 1 |
| 5 | Analog Input | Real power | kW | Present Value | R | R |  |
| 6 | Analog Input | Reactive power | kVARh | Present Value | R | R |  |
| 7 | Analog Input | Apparent power | kVARh | Present Value | R | R |  |
| 8 | Analog Input | Power factor | % PF | Present Value | R | R |  |
| 9 | Analog Input | Current total | Amps | Present Value | R | R |  |
| 10 | Analog Input | Current average | Amps | Present Value | R | R |  |
| 11 | Analog Input | Voltage line-neutral | Volts-N | Present Value | R | R |  |
| 12 | Analog Input | Voltage line-line | Volts-L | Present Value | R | R |  |
| 13 | Analog Input | Frequency | Hz | Present Value | R | R |  |
| 14 | Analog Input | Phase angle | Degree | Present Value | R | R |  |
| 15 | Analog Input | Real power phase A | kW | Present Value | R | R |  |
| 16 | Analog Input | Real power phase B | kW | Present Value | R | R |  |
| 17 | Analog Input | Real power phase C | kW | Present Value | R | R |  |
| 18 | Analog Input | Reactive power phase A | kVAR | Present Value | R | R |  |
| 19 | Analog Input | Reactive power phase B | kVAR | Present Value | R | R |  |
| 20 | Analog Input | Reactive power phase C | kVAR | Present Value | R | R |  |
| 21 | Analog Input | Apparent power phase A | kVA | Present Value | R | R |  |
| 22 | Analog Input | Apparent power phase B | kVA | Present Value | R | R |  |
| 23 | Analog Input | Apparent power phase C | kVA | Present Value | R | R |  |
| 24 | Analog Input | Power factor phase A | % PF | Present Value | R | R |  |
| 25 | Analog Input | Power factor phase B | % PF | Present Value | R | R |  |
| 26 | Analog Input | Power factor phase C | % PF | Present Value | R | R |  |
| 27 | Analog Input | Current phase A | Amps | Present Value | R | R |  |
| 28 | Analog Input | Current phase B | Amps | Present Value | R | R |  |
| 29 | Analog Input | Current phase C | Amps | Present Value | R | R |  |
| 30 | Analog Input | Voltage line-neutral phase A-N | Volts-N | Present Value | R | R |  |
| 31 | Analog Input | Voltage line-neutral phase B-N | Volts-N | Present Value | R | R |  |
| 32 | Analog Input | Voltage line-neutral phase C-N | Volts-N | Present Value | R | R |  |
| 33 | Analog Input | Voltage line-line phase A-B | Volts-L | Present Value | R | R |  |
| 34 | Analog Input | Voltage line-line phase B-C | Volts-L | Present Value | R | R |  |
| 35 | Analog Input | Voltage line-line phase C-A | Volts-L | Present Value | R | R |  |
| 36 | Analog Input | Phase angle phase A | Degree | Present Value | R | R |  |
| 37 | Analog Input | Phase angle phase B | Degree | Present Value | R | R |  |
| 38 | Analog Input | Phase angle phase C | Degree | Present Value | R | R |  |
| 39 | Analog Input | Reserve A | No units | Present Value | R | R |  |
| 40 | Analog Input | Reserve B | No units | Present Value | R | R |  |
| 41 | Analog Input | Reserve C | No units | Present Value | R | R |  |
| 42 | Analog Input | External Input 1 | Pulse | Present Value | R | R | 2 |
| 43 | Analog Input | External Input 2 | Pulse | Present Value | R | R | 2 |

- Can only clear using ModBus RTU.  Jumper J2 must be closed.  BACnet IP Ethernet module must be removed to access ModBus RTU.

- Can only clear using ModBus RTU.  Jumper J2 must be closed.  BACnet IP Ethernet module must be removed to access ModBus RTU.

- E-Mon D-Mon BACnet Object Descriptors: IDR8 and IDR16

| Instance ID | BACnet Object | Description | Units | BACnet Property | IDR | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Analog Input | Usage Channel 1 | Pulse * Pulse Value | Present Value | R | 1 |
| 2 | Analog Input | Usage Channel 2 | Pulse * Pulse Value | Present Value | R | 1 |
| 3 | Analog Input | Usage Channel 3 | Pulse * Pulse Value | Present Value | R | 1 |
| 4 | Analog Input | Usage Channel 4 | Pulse * Pulse Value | Present Value | R | 1 |
| 5 | Analog Input | Usage Channel 5 | Pulse * Pulse Value | Present Value | R | 1 |
| 6 | Analog Input | Usage Channel 6 | Pulse * Pulse Value | Present Value | R | 1 |
| 7 | Analog Input | Usage Channel 7 | Pulse * Pulse Value | Present Value | R | 1 |
| 8 | Analog Input | Usage Channel 8 | Pulse * Pulse Value | Present Value | R | 1 |
| 9 | Analog Input | Usage Channel 9 | Pulse * Pulse Value | Present Value | R | 1 |
| 10 | Analog Input | Usage Channel 10 | Pulse * Pulse Value | Present Value | R | 1 |
| 11 | Analog Input | Usage Channel 11 | Pulse * Pulse Value | Present Value | R | 1 |
| 12 | Analog Input | Usage Channel 12 | Pulse * Pulse Value | Present Value | R | 1 |
| 13 | Analog Input | Usage Channel 13 | Pulse * Pulse Value | Present Value | R | 1 |
| 14 | Analog Input | Usage Channel 14 | Pulse * Pulse Value | Present Value | R | 1 |
| 15 | Analog Input | Usage Channel 15 | Pulse * Pulse Value | Present Value | R | 1 |
| 16 | Analog Input | Usage Channel 16 | Pulse * Pulse Value | Present Value | R | 1 |
| 17 | Analog Input | Demand Channel 1 | Demand * Pulse Value | Present Value | R |  |
| 18 | Analog Input | Demand Channel 2 | Demand * Pulse Value | Present Value | R |  |
| 19 | Analog Input | Demand Channel 3 | Demand * Pulse Value | Present Value | R |  |
| 20 | Analog Input | Demand Channel 4 | Demand * Pulse Value | Present Value | R |  |
| 21 | Analog Input | Demand Channel 5 | Demand * Pulse Value | Present Value | R |  |
| 22 | Analog Input | Demand Channel 6 | Demand * Pulse Value | Present Value | R |  |
| 23 | Analog Input | Demand Channel 7 | Demand * Pulse Value | Present Value | R |  |
| 24 | Analog Input | Demand Channel 8 | Demand * Pulse Value | Present Value | R |  |
| 25 | Analog Input | Demand Channel 9 | Demand * Pulse Value | Present Value | R |  |
| 26 | Analog Input | Demand Channel 10 | Demand * Pulse Value | Present Value | R |  |
| 27 | Analog Input | Demand Channel 11 | Demand * Pulse Value | Present Value | R |  |
| 28 | Analog Input | Demand Channel 12 | Demand * Pulse Value | Present Value | R |  |
| 29 | Analog Input | Demand Channel 13 | Demand * Pulse Value | Present Value | R |  |
| 30 | Analog Input | Demand Channel 14 | Demand * Pulse Value | Present Value | R |  |
| 31 | Analog Input | Demand Channel 15 | Demand * Pulse Value | Present Value | R |  |
| 32 | Analog Input | Demand Channel 16 | Demand * Pulse Value | Present Value | R |  |

- To clear usage channels, select reset kW/kWh on the display menu of the IDR.  Jumper J6 must be closed.

| Instance ID | BACnet Object | BACnet Property | IDR | Notes |
| --- | --- | --- | --- | --- |
| BACnet Device ID | Device | Object identifier | R |  |
| BACnet Device ID | Device | Object name | R |  |
| BACnet Device ID | Device | Object type | R |  |
| BACnet Device ID | Device | System status | R/W |  |
| BACnet Device ID | Device | Vendor name | R |  |
| BACnet Device ID | Device | Vendor Identifier | R |  |
| BACnet Device ID | Device | Model name | R |  |
| BACnet Device ID | Device | Firmware revision | R |  |
| BACnet Device ID | Device | Application software version | R |  |
| BACnet Device ID | Device | Location | R/W |  |
| BACnet Device ID | Device | Description | R/W |  |
| BACnet Device ID | Device | Protocol version | R |  |
| BACnet Device ID | Device | Protocol services supported | R |  |
| BACnet Device ID | Device | Protocol object types supported | R |  |
| BACnet Device ID | Device | Protocol revision | R |  |
| BACnet Device ID | Device | Object list | R |  |
| BACnet Device ID | Device | Max APDU length supported | R |  |
| BACnet Device ID | Device | Segmentation supported | R |  |
| BACnet Device ID | Device | Local time | R |  |
| BACnet Device ID | Device | Local date | R |  |
| BACnet Device ID | Device | APDU timeout | R/W |  |
| BACnet Device ID | Device | Number of APDU retries | R/W |  |
| BACnet Device ID | Device | Device address binding | R |  |

With an IDR16 each channel 1 through 16 represents the IDR16 meter jack inputs 1 through 16.

With an IDR8 each channel 1 through 8 represents the IDR8 meter jack inputs 1 through 8.

Units are pulse counts.  The pulse value guide in Table 1 below represents the kilowatt-hour value of the meter size (amperage) plugged into the IDR meter jack.  To calculate kWh Usage and kW Demand take the number of pulses multiplied by the meter pulse value to determine total kWh and kW.  Set the EMS/BMS front end to multiply the pulse values by the pulse counts. See Table 1 below for the different meter sizes (Amperage) Watt Hour pulse values.

| Table 1 E-Mon Class 1000 & 2000 Meter Size Pulse Value Guide |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 25 Amp | 50 Amp | 100 Amp | 200 Amp | 400 Amp | 800 Amp | 1600 Amp | 3200 Amp |
| Base Watt Hour Value per Pulse for legacy E-Mon meters* (serial numbers starting with 1203XXXX and earlier) |  |  |  |  |  |  |  |
| 7.8125 | 15.625 | 31.25 | 62.50 | 125.00 | 250.00 | 500.00 | 1000.00 |
| Base Watt Hour Value per Pulse* (serial numbers above 1203XXXX) |  |  |  |  |  |  |  |
| 0.48828 | 0.97656 | 1.95313 | 3.90625 | 7.8125 | 15.625 | 31.25 | 62.50 |

*E-Mon meters support paralleling of 3 sets of up to current sensors; the Multipliers listed in Table 1 are based on 1 set of current sensors. When multiple sets of current sensors are installed in parallel, the final multiplier will be the product of the base multiplier listed in Table 1 times the number of sets of current sensors in parallel. If the meter is using more than 1 set of current sensors, be sure to also factor the number of sets into the Pulse Value.

Formula for calculating Multiplier = Base Multiplier multiplied by the number of sets of Current Sensors in Parallel.

Example: Calculate the Multiplier for a meter of 120/208 Volt, 3-Phase, 200 Amp, 3 sets of Current Sensors in parallel for a legacy meter.

The final Multiplier is 187.50 which is the result of 62.50 multiplied by 3.  The final Pulse Value is 187.50 Watt Hours per pulse.

Example: Calculate the Multiplier for a meter of 120/208 Volt, 3-Phase, 200 Amp, 3 sets of Current Sensors in parallel for a non legacy meter.

The final Multiplier is 11.71875 which is the result of 3.90625 multiplied by 3.  The final Pulse Value is 11.71875 Watt Hours per pulse.

E-Mon D-Mon BACnet Object Descriptors: Legacy IDR

| Instance ID | BACnet Object | Description | Units | BACnet Property | Legacy IDR | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Analog Input | Usage Channel 1 | Pulse | Present Value | R | 1 |
| 2 | Analog Input | Usage Channel 2 | Pulse | Present Value | R | 1 |
| 3 | Analog Input | Usage Channel 3 | Pulse | Present Value | R | 1 |
| 4 | Analog Input | Usage Channel 4 | Pulse | Present Value | R | 1 |
| 5 | Analog Input | Usage Channel 5 | Pulse | Present Value | R | 1 |
| 6 | Analog Input | Usage Channel 6 | Pulse | Present Value | R | 1 |
| 7 | Analog Input | Usage Channel 7 | Pulse | Present Value | R | 1 |
| 8 | Analog Input | Usage Channel 8 | Pulse | Present Value | R | 1 |
| 9 | Analog Input | Usage Channel 9 | Pulse | Present Value | R | 1 |
| 10 | Analog Input | Usage Channel 10 | Pulse | Present Value | R | 1 |
| 11 | Analog Input | Usage Channel 11 | Pulse | Present Value | R | 1 |
| 12 | Analog Input | Usage Channel 12 | Pulse | Present Value | R | 1 |
| 13 | Analog Input | Usage Channel 13 | Pulse | Present Value | R | 1 |
| 14 | Analog Input | Usage Channel 14 | Pulse | Present Value | R | 1 |
| 15 | Analog Input | Usage Channel 15 | Pulse | Present Value | R | 1 |
| 16 | Analog Input | Usage Channel 16 | Pulse | Present Value | R | 1 |
| 33 | Analog Input | Demand Channel 1 | Peak Demand | Present Value | R |  |
| 34 | Analog Input | Demand Channel 2 | Peak Demand | Present Value | R |  |
| 35 | Analog Input | Demand Channel 3 | Peak Demand | Present Value | R |  |
| 36 | Analog Input | Demand Channel 4 | Peak Demand | Present Value | R |  |
| 37 | Analog Input | Demand Channel 5 | Peak Demand | Present Value | R |  |
| 38 | Analog Input | Demand Channel 6 | Peak Demand | Present Value | R |  |
| 39 | Analog Input | Demand Channel 7 | Peak Demand | Present Value | R |  |
| 40 | Analog Input | Demand Channel 8 | Peak Demand | Present Value | R |  |
| 41 | Analog Input | Demand Channel 9 | Peak Demand | Present Value | R |  |
| 42 | Analog Input | Demand Channel 10 | Peak Demand | Present Value | R |  |
| 43 | Analog Input | Demand Channel 11 | Peak Demand | Present Value | R |  |
| 44 | Analog Input | Demand Channel 12 | Peak Demand | Present Value | R |  |
| 45 | Analog Input | Demand Channel 13 | Peak Demand | Present Value | R |  |
| 46 | Analog Input | Demand Channel 14 | Peak Demand | Present Value | R |  |
| 47 | Analog Input | Demand Channel 15 | Peak Demand | Present Value | R |  |
| 48 | Analog Input | Demand Channel 16 | Peak Demand | Present Value | R |  |

- Can only clear using ModBus RTU.  Jumper J7 must be closed.  BACnet IP Ethernet module must be removed to access ModBus RTU.

- Can only clear using ModBus RTU.  Jumper J7 must be closed.  BACnet IP Ethernet module must be removed to access ModBus RTU.

E-Mon D-Mon LonWorks Point Map: Class 3400 and 5000 Meters

| Network Variable Name | SNVT Type | Description | Units | CL3400 CL5000 | Notes |
| --- | --- | --- | --- | --- | --- |
| nvoKWh_Del | SNVT_count_inc_f | Energy delivered | kWh | R | 1 |
| nvoKWh_Rec | SNVT_count_inc_f | Energy received | kWh | R | 1 |
| nvoKVarh_Del | SNVT_count_inc_f | Reactive energy delivered | kVARh | R | 1 |
| nvoKVarh_Rec | SNVT_count_inc_f | Reactive energy received | kVARh | R | 1 |
| nvoReal_Pwr | SNVT_count_inc_f | Real power | kW | R |  |
| nvoReact_Pwr | SNVT_count_inc_f | Reactive power | kVAR | R |  |
| nvoAppar_Pwr | SNVT_count_inc_f | Apparent power | kVA | R |  |
| nvoPwr_Fact | SNVT_pwr_fact_f | Power factor | % PF | R |  |
| nvoPeak_Dem | SNVT_count_inc_f | Peak demand | kW | R |  |
| nvoCurrent_Avg | SNVT_amp_f | Current average | Amps | R |  |
| nvoVolt_LN | SNVT_volt_f | Voltage line-neutral | Volts-N | R |  |
| nvoVolt_LL | SNVT_volt_f | Voltage line-line | Volts-L | R |  |
| nvoFrequency | SNVT_freq_f | Frequency | Hz | R |  |
| nvoPhase_Angle | SNVT_count_inc_f | Phase angle | Degree | R |  |
| nvoReal_Pwr_PhA | SNVT_count_inc_f | Real power, phase A | kW | R |  |
| nvoReal_Pwr_PhB | SNVT_count_inc_f | Real power, phase B | kW | R |  |
| nvoReal_Pwr_PhC | SNVT_count_inc_f | Real power, phase C | kW | R |  |
| nvoReact_Pwr_PhA | SNVT_count_inc_f | Reactive power, phase A | kVAR | R |  |
| nvoReact_Pwr_PhB | SNVT_count_inc_f | Reactive power, phase B | kVAR | R |  |
| nvoReact_Pwr_PhC | SNVT_count_inc_f | Reactive power, phase C | kVAR | R |  |
| nvoAppar_Pwr_PhA | SNVT_count_inc_f | Apparent power, phase A | kVA | R |  |
| nvoAppar_Pwr_PhB | SNVT_count_inc_f | Apparent power, phase B | kVA | R |  |
| nvoAppar_Pwr_PhC | SNVT_count_inc_f | Apparent power, phase C | kVA | R |  |
| nvoPwr_Fact_PhA | SNVT_pwr_fact_f | Power factor, phase A | % PF | R |  |
| nvoPwr_Fact_PhB | SNVT_pwr_fact_f | Power factor, phase B | % PF | R |  |
| nvoPwr_Fact_PhC | SNVT_pwr_fact_f | Power factor, phase C | % PF | R |  |
| nvoCurrent_PhA | SNVT_amp_f | Current, phase A | Amps | R |  |
| nvoCurrent_PhB | SNVT_amp_f | Current, phase B | Amps | R |  |
| nvoCurrent_PhC | SNVT_amp_f | Current, phase C | Amps | R |  |
| nvoVolt_LN_PhA_N | SNVT_volt_f | Voltage, line to neutral, phase A-N | Volts-N | R |  |
| nvoVolt_LN_PhB_N | SNVT_volt_f | Voltage, line to neutral, phase B-N | Volts-N | R |  |
| nvoVolt_LN_PhC_N | SNVT_volt_f | Voltage, line to neutral, phase C-N | Volts-N | R |  |
| nvoVolt_LL_PhA_B | SNVT_volt_f | Voltage, line to line, phase A-B | Volts-L | R |  |
| nvoVolt_LL_PhB_C | SNVT_volt_f | Voltage, line to line, phase B-C | Volts-L | R |  |
| nvoVolt_LL_PhC_A | SNVT_volt_f | Voltage, line to line, phase C-A | Volts-L | R |  |
| nvoPhase_AngleA | SNVT_count_inc_f | Phase angle, phase A | Degree | R |  |
| nvoPhase_AngleB | SNVT_count_inc_f | Phase angle, phase B | Degree | R |  |
| nvoPhase_AngleC | SNVT_count_inc_f | Phase angle, phase C | Degree | R |  |
| nvoReserve_A | SNVT_count_f | Reserve A | No units | R |  |
| nvoReserve_B | SNVT_count_f | Reserve B | No units | R |  |
| nvoReserve_C | SNVT_count_f | Reserve C | No units | R |  |
| nvoExt_Input_1 | SNVT_count_f | External Input 1 | Pulse | R | 2 |
| nvoExt_Input_2 | SNVT_count_f | External Input 2 | Pulse | R | 2 |

- To clear single meter kWh/kVARh, select reset kW/kWh on the display menu of the meter.  This function will also reset external inputs.  Jumper J6 must be closed.

- External inputs are standard on Class 5000 meters and optional on Class 3400 meters (Part of Expanded Feature Package).  To clear external inputs, select reset kW/kWh on the display menu of the meter.  This function will also reset kW/kVARh.  Jumper J6 must be closed.

E-Mon D-Mon LonWorks Point Map: Legacy Class 3000 and 5000 Meters

| Network Variable Name | SNVT Type | Description | Units | Legacy CL3000 | Legacy CL5000 | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| nvoEnergy_Delive | SNVT_count_inc_f | Energy delivered | kWh | R | R | 1 |
| nvoEnergy_Receiv | SNVT_count_inc_f | Energy received | kWh | R | R | 1 |
| nvoReac_NRG_Del | SNVT_count_inc_f | Reactive energy delivered | kVARh | R | R | 1 |
| nvoReac_NRG_Rec | SNVT_count_inc_f | Reactive energy received | kVARh | R | R | 1 |
| nvoReal_pwr | SNVT_count_inc_f | Real power | kW | R | R |  |
| nvoReactive_pwr | SNVT_count_inc_f | Reactive power | kVARh | R | R |  |
| nvoApparent_pwr | SNVT_count_inc_f | Apparent power | kVARh | R | R |  |
| nvopwr_factor | SNVT_lev_percent | Power factor | % PF | R | R |  |
| nvoCurrent_total | SNVT_count_inc_f | Current total | Amps | R | R |  |
| nvoCurrent_Avg | SNVT_count_inc_f | Current average | Amps | R | R |  |
| nvoVoltage_L_N | SNVT_count_inc_f | Voltage line-neutral | Volts-N | R | R |  |
| nvoVoltage_L_L | SNVT_count_inc_f | Voltage line-line | Volts-L | R | R |  |
| nvoFrequency | SNVT_freq_hz | Frequency | Hz | R | R |  |
| nvoPhangle | SNVT_angle_deg | Phase angle | Degree | R | R |  |
| nvoReal_pwr_PhA | SNVT_count_inc_f | Real power, phase A | kW | R | R |  |
| nvoReal_pwr_PhB | SNVT_count_inc_f | Real power, phase B | kW | R | R |  |
| nvoReal_pwr_PhC | SNVT_count_inc_f | Real power, phase C | kW | R | R |  |
| nvoReact_pwr_PhA | SNVT_count_inc_f | Reactive power, phase A | kVAR | R | R |  |
| nvoReact_pwr_PhB | SNVT_count_inc_f | Reactive power, phase B | kVAR | R | R |  |
| nvoReact_pwr_PhC | SNVT_count_inc_f | Reactive power, phase C | kVAR | R | R |  |
| nvoAppar_pwr_PhA | SNVT_count_inc_f | Apparent power, phase A | kVA | R | R |  |
| nvoAppar_pwr_PhB | SNVT_count_inc_f | Apparent power, phase B | kVA | R | R |  |
| nvoAppar_pwr_PhC | SNVT_count_inc_f | Apparent power, phase C | kVA | R | R |  |
| nvopwr_factr_PhA | SNVT_lev_percent | Power factor, phase A | % PF | R | R |  |
| nvopwr_factr_PhB | SNVT_lev_percent | Power factor, phase B | % PF | R | R |  |
| nvopwr_factr_PhC | SNVT_lev_percent | Power factor, phase C | % PF | R | R |  |
| nvoCurrent_PhA | SNVT_count_inc_f | Current, phase A | Amps | R | R |  |
| nvoCurrent_PhB | SNVT_count_inc_f | Current, phase B | Amps | R | R |  |
| nvoCurrent_PhC | SNVT_count_inc_f | Current, phase C | Amps | R | R |  |
| nvoVlt_L_N_PhA_N | SNVT_count_inc_f | Voltage, line to neutral, phase A-N | Volts-N | R | R |  |
| nvoVlt_L_N_PhB_N | SNVT_count_inc_f | Voltage, line to neutral, phase B-N | Volts-N | R | R |  |
| nvoVlt_L_N_PhC_N | SNVT_count_inc_f | Voltage, line to neutral, phase C-N | Volts-N | R | R |  |
| nvoVlt_L_L_PhA_B | SNVT_count_inc_f | Voltage, line to line, phase A-B | Volts-L | R | R |  |
| nvoVlt_L_L_PhB_C | SNVT_count_inc_f | Voltage, line to line, phase B-C | Volts-L | R | R |  |
| nvoVlt_L_L_PhC_A | SNVT_count_inc_f | Voltage, line to line, phase C-A | Volts-L | R | R |  |
| nvoPhAngle_PhA | SNVT_angle_deg | Phase angle, phase A | Degree | R | R |  |
| nvoPhAngle_PhB | SNVT_angle_deg | Phase angle, phase B | Degree | R | R |  |
| nvoPhAngle_PhC | SNVT_angle_deg | Phase angle, phase C | Degree | R | R |  |
| nvoReserve_A | SNVT_count_f | Reserve A | No units | R | R |  |
| nvoReserve_B | SNVT_count_f | Reserve B | No units | R | R |  |
| nvoReserve_C | SNVT_count_f | Reserve C | No units | R | R |  |
| nvoExt_Input_1 | SNVT_count_f | External Input 1 | Pulse | R | R | 2 |
| nvoExt_Input_2 | SNVT_count_f | External Input 2 | Pulse | R | R | 2 |

- Can only clear using ModBus RTU.  Jumper J2 must be closed.  LonWorks module must be removed to access ModBus RTU.

- Can only clear using ModBus RTU.  Jumper J2 must be closed.  LonWorks module must be removed to access ModBus RTU.

E-Mon D-Mon LonWorks Point Map: IDR8 and IDR16

| Network Variable Name | Function Block Index | SNVT Type | Description | Units | IDR | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| nvoUsageCh01 | 1 | SNVT_count_f | Usage Channel 1 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh02 | 2 | SNVT_count_f | Usage Channel 2 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh03 | 3 | SNVT_count_f | Usage Channel 3 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh04 | 4 | SNVT_count_f | Usage Channel 4 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh05 | 5 | SNVT_count_f | Usage Channel 5 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh06 | 6 | SNVT_count_f | Usage Channel 6 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh07 | 7 | SNVT_count_f | Usage Channel 7 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh08 | 8 | SNVT_count_f | Usage Channel 8 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh09 | 9 | SNVT_count_f | Usage Channel 9 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh10 | 10 | SNVT_count_f | Usage Channel 10 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh11 | 11 | SNVT_count_f | Usage Channel 11 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh12 | 12 | SNVT_count_f | Usage Channel 12 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh13 | 13 | SNVT_count_f | Usage Channel 13 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh14 | 14 | SNVT_count_f | Usage Channel 14 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh15 | 15 | SNVT_count_f | Usage Channel 15 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh16 | 16 | SNVT_count_f | Usage Channel 16 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh17 | 17 | SNVT_count_f | Usage Channel 17 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh18 | 18 | SNVT_count_f | Usage Channel 18 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh19 | 19 | SNVT_count_f | Usage Channel 19 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh20 | 20 | SNVT_count_f | Usage Channel 20 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh21 | 21 | SNVT_count_f | Usage Channel 21 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh22 | 22 | SNVT_count_f | Usage Channel 22 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh23 | 23 | SNVT_count_f | Usage Channel 23 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh24 | 24 | SNVT_count_f | Usage Channel 24 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh25 | 25 | SNVT_count_f | Usage Channel 25 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh26 | 26 | SNVT_count_f | Usage Channel 26 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh27 | 27 | SNVT_count_f | Usage Channel 27 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh28 | 28 | SNVT_count_f | Usage Channel 28 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh29 | 29 | SNVT_count_f | Usage Channel 29 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh30 | 30 | SNVT_count_f | Usage Channel 30 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh31 | 31 | SNVT_count_f | Usage Channel 31 | Pulse * Pulse Value | R | 1 |
| nvoUsageCh32 | 32 | SNVT_count_f | Usage Channel 32 | Pulse * Pulse Value | R | 1 |
| nvoDemandCh01 | 33 | SNVT_count_f | Demand Channel 1 | Demand * Pulse Value | R |  |
| nvoDemandCh02 | 34 | SNVT_count_f | Demand Channel 2 | Demand * Pulse Value | R |  |
| nvoDemandCh03 | 35 | SNVT_count_f | Demand Channel 3 | Demand * Pulse Value | R |  |
| nvoDemandCh04 | 36 | SNVT_count_f | Demand Channel 4 | Demand * Pulse Value | R |  |
| nvoDemandCh05 | 37 | SNVT_count_f | Demand Channel 5 | Demand * Pulse Value | R |  |
| nvoDemandCh06 | 38 | SNVT_count_f | Demand Channel 6 | Demand * Pulse Value | R |  |
| nvoDemandCh07 | 39 | SNVT_count_f | Demand Channel 7 | Demand * Pulse Value | R |  |
| nvoDemandCh08 | 40 | SNVT_count_f | Demand Channel 8 | Demand * Pulse Value | R |  |
| nvoDemandCh09 | 41 | SNVT_count_f | Demand Channel 9 | Demand * Pulse Value | R |  |
| nvoDemandCh10 | 42 | SNVT_count_f | Demand Channel 10 | Demand * Pulse Value | R |  |
| nvoDemandCh11 | 43 | SNVT_count_f | Demand Channel 11 | Demand * Pulse Value | R |  |
| nvoDemandCh12 | 44 | SNVT_count_f | Demand Channel 12 | Demand * Pulse Value | R |  |
| nvoDemandCh13 | 45 | SNVT_count_f | Demand Channel 13 | Demand * Pulse Value | R |  |
| nvoDemandCh14 | 46 | SNVT_count_f | Demand Channel 14 | Demand * Pulse Value | R |  |
| nvoDemandCh15 | 47 | SNVT_count_f | Demand Channel 15 | Demand * Pulse Value | R |  |
| nvoDemandCh16 | 48 | SNVT_count_f | Demand Channel 16 | Demand * Pulse Value | R |  |
| nvoDemandCh17 | 49 | SNVT_count_f | Demand Channel 17 | Demand * Pulse Value | R |  |
| nvoDemandCh18 | 50 | SNVT_count_f | Demand Channel 18 | Demand * Pulse Value | R |  |
| nvoDemandCh19 | 51 | SNVT_count_f | Demand Channel 19 | Demand * Pulse Value | R |  |
| nvoDemandCh20 | 52 | SNVT_count_f | Demand Channel 20 | Demand * Pulse Value | R |  |
| nvoDemandCh21 | 53 | SNVT_count_f | Demand Channel 21 | Demand * Pulse Value | R |  |
| nvoDemandCh22 | 54 | SNVT_count_f | Demand Channel 22 | Demand * Pulse Value | R |  |
| nvoDemandCh23 | 55 | SNVT_count_f | Demand Channel 23 | Demand * Pulse Value | R |  |
| nvoDemandCh24 | 56 | SNVT_count_f | Demand Channel 24 | Demand * Pulse Value | R |  |
| nvoDemandCh25 | 57 | SNVT_count_f | Demand Channel 25 | Demand * Pulse Value | R |  |
| nvoDemandCh26 | 58 | SNVT_count_f | Demand Channel 26 | Demand * Pulse Value | R |  |
| nvoDemandCh27 | 59 | SNVT_count_f | Demand Channel 27 | Demand * Pulse Value | R |  |
| nvoDemandCh28 | 60 | SNVT_count_f | Demand Channel 28 | Demand * Pulse Value | R |  |
| nvoDemandCh29 | 61 | SNVT_count_f | Demand Channel 29 | Demand * Pulse Value | R |  |
| nvoDemandCh30 | 62 | SNVT_count_f | Demand Channel 30 | Demand * Pulse Value | R |  |
| nvoDemandCh31 | 63 | SNVT_count_f | Demand Channel 31 | Demand * Pulse Value | R |  |
| nvoDemandCh32 | 64 | SNVT_count_f | Demand Channel 32 | Demand * Pulse Value | R |  |
| nviResetUsageCh | 65 | SNVT_count | Reset Usage Channel | Integer Channel | R/W | 1 |
| nvoRTC_DateTime | 66 | SNVT_time_stamp | RTC Date, Time Read | Date, Time | R |  |
| nviRTC_DateTime | 66 | SNVT_time_stamp | RTC Date, Time Set | Date, Time | R/W | 2 |
| nvoIntervalData | 67 | SNVT_reg_val_ts | Interval Data Pulse Read | Integer Pulses, Date, Time | R | 3 |
| nviIntDataTime | 67 | SNVT_time_stamp | Interval Date, Time Set | Date, Time | R/W | 3 |
| nviIntDataChan | 67 | SNVT_count | Interval Data Channel Set | Integer Channel | R/W | 3 |
| nviIntDataPeriod | 67 | SNVT_count | Interval Data Window Set | Minutes | R/W | 3 |
| nvoStatus | 0 | SNVT_obj_status | Function Block Status | Function Block Status | R | 4 |
| nviRequest | 0 | SNVT_obj_request | Function Block Request | Function Block Enable/Disable | R/W | 4 |
| nvoFileDirectory | 0 | SNVT_address | File Directory | Config File Directory | R |  |

- To clear all usage channels, select reset kW/kWh on the display menu of the IDR.  Jumper J6 must be closed.  To clear individual channels, set nviResetUsageCh to the desired channel.  For example, set nviResetUsageCh to 1 to reset nvoUsageCh01.

- To set the real time clock, set nviRTC_DateTime to the desired date and time.

- NvoIntervalData will display the number of pulses for the selected interval period and channel.  For example, set nviIntDataTime to 6/1/2012 13:15:00 to read the number of pulses from 13:15:00 to 13:29:59.  The second status bit value will be 0 if no error has occurred.  The interval data period window can be set to read 15 or 5 minutes using the nviIntDataPeriod.  This value will not change the default interval data period value of 15 minutes.  NviIntDataChan will select the usage channel.  For example, set nviIntDataChan to 1 to read the interval data for nvoUsageCh01.

- NviRequest commands can disable or enable functional blocks.  Any changes will be saved even after powered down.  Set nviRequest to 0,RQ_DISABLE to disable all functional blocks.  Set nviRequest to 0,RQ_ENABLE to enable all function blocks.  Set nviRequest to 1,RQ_DISABLE to disable only functional block 1.  The first value of nvoStatus is the functional block, and the 3rd bit in the bit array is 1 when disabled.

With an IDR16 each channel 1 through 16 represents the IDR16 meter jack inputs 1 through 16.

With an IDR8 each channel 1 through 8 represents the IDR8 meter jack inputs 1 through 8.

Units are pulse counts.  The pulse value guide in Table 1 below represents the kilowatt-hour value of the meter size (amperage) plugged into the IDR meter jack.  To calculate kWh Usage and kW Demand take the number of pulses multiplied by the meter pulse value to determine total kWh and kW.  Set the EMS/BMS front end to multiply the pulse values by the pulse counts. See Table 1 below for the different meter sizes (Amperage) Watt Hour pulse values.

| Table 1 E-Mon Class 1000 & 2000 Meter Size Pulse Value Guide |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 25 Amp | 50 Amp | 100 Amp | 200 Amp | 400 Amp | 800 Amp | 1600 Amp | 3200 Amp |
| Base Watt Hour Value per Pulse for legacy E-Mon meters* (serial numbers starting with 1203XXXX and earlier) |  |  |  |  |  |  |  |
| 7.8125 | 15.625 | 31.25 | 62.50 | 125.00 | 250.00 | 500.00 | 1000.00 |
| Base Watt Hour Value per Pulse* (serial numbers above 1203XXXX) |  |  |  |  |  |  |  |
| 0.48828 | 0.97656 | 1.95313 | 3.90625 | 7.8125 | 15.625 | 31.25 | 62.50 |

*E-Mon meters support paralleling of 3 sets of up to current sensors; the Multipliers listed in Table 1 are based on 1 set of current sensors. When multiple sets of current sensors are installed in parallel, the final multiplier will be the product of the base multiplier listed in Table 1 times the number of sets of current sensors in parallel. If the meter is using more than 1 set of current sensors, be sure to also factor the number of sets into the Pulse Value.

Formula for calculating Multiplier = Base Multiplier multiplied by the number of sets of Current Sensors in Parallel.

Example: Calculate the Multiplier for a meter of 120/208 Volt, 3-Phase, 200 Amp, 3 sets of Current Sensors in parallel for a legacy meter.

The final Multiplier is 187.50 which is the result of 62.50 multiplied by 3.  The final Pulse Value is 187.50 Watt Hours per pulse.

Example: Calculate the Multiplier for a meter of 120/208 Volt, 3-Phase, 200 Amp, 3 sets of Current Sensors in parallel for a non legacy meter.

The final Multiplier is 11.71875 which is the result of 3.90625 multiplied by 3.  The final Pulse Value is 11.71875 Watt Hours per pulse.

E-Mon D-Mon LonWorks Point Map: Legacy IDR

| Network Variable Name | SNVT Type | Description | Units | Legacy IDR | Notes |
| --- | --- | --- | --- | --- | --- |
| nvoPM-F_EnrgCh01 | SNVT_count_f | Usage Channel 1 | Pulse | R | 1 |
| nvoPM-F_EnrgCh02 | SNVT_count_f | Usage Channel 2 | Pulse | R | 1 |
| nvoPM-F_EnrgCh03 | SNVT_count_f | Usage Channel 3 | Pulse | R | 1 |
| nvoPM-F_EnrgCh04 | SNVT_count_f | Usage Channel 4 | Pulse | R | 1 |
| nvoPM-F_EnrgCh05 | SNVT_count_f | Usage Channel 5 | Pulse | R | 1 |
| nvoPM-F_EnrgCh06 | SNVT_count_f | Usage Channel 6 | Pulse | R | 1 |
| nvoPM-F_EnrgCh07 | SNVT_count_f | Usage Channel 7 | Pulse | R | 1 |
| nvoPM-F_EnrgCh08 | SNVT_count_f | Usage Channel 8 | Pulse | R | 1 |
| nvoPM-F_EnrgCh09 | SNVT_count_f | Usage Channel 9 | Pulse | R | 1 |
| nvoPM-F_EnrgCh10 | SNVT_count_f | Usage Channel 10 | Pulse | R | 1 |
| nvoPM-F_EnrgCh11 | SNVT_count_f | Usage Channel 11 | Pulse | R | 1 |
| nvoPM-F_EnrgCh12 | SNVT_count_f | Usage Channel 12 | Pulse | R | 1 |
| nvoPM-F_EnrgCh13 | SNVT_count_f | Usage Channel 13 | Pulse | R | 1 |
| nvoPM-F_EnrgCh14 | SNVT_count_f | Usage Channel 14 | Pulse | R | 1 |
| nvoPM-F_EnrgCh15 | SNVT_count_f | Usage Channel 15 | Pulse | R | 1 |
| nvoPM-F_EnrgCh16 | SNVT_count_f | Usage Channel 16 | Pulse | R | 1 |
| nvoPM-F_DmndCh01 | SNVT_count_f | Demand Channel 1 | Pulse | R | 2 |
| nvoPM-F_DmndCh02 | SNVT_count_f | Demand Channel 2 | Pulse | R | 2 |
| nvoPM-F_DmndCh03 | SNVT_count_f | Demand Channel 3 | Pulse | R | 2 |
| nvoPM-F_DmndCh04 | SNVT_count_f | Demand Channel 4 | Pulse | R | 2 |
| nvoPM-F_DmndCh05 | SNVT_count_f | Demand Channel 5 | Pulse | R | 2 |
| nvoPM-F_DmndCh06 | SNVT_count_f | Demand Channel 6 | Pulse | R | 2 |
| nvoPM-F_DmndCh07 | SNVT_count_f | Demand Channel 7 | Pulse | R | 2 |
| nvoPM-F_DmndCh08 | SNVT_count_f | Demand Channel 8 | Pulse | R | 2 |
| nvoPM-F_DmndCh09 | SNVT_count_f | Demand Channel 9 | Pulse | R | 2 |
| nvoPM-F_DmndCh10 | SNVT_count_f | Demand Channel 10 | Pulse | R | 2 |
| nvoPM-F_DmndCh11 | SNVT_count_f | Demand Channel 11 | Pulse | R | 2 |
| nvoPM-F_DmndCh12 | SNVT_count_f | Demand Channel 12 | Pulse | R | 2 |
| nvoPM-F_DmndCh13 | SNVT_count_f | Demand Channel 13 | Pulse | R | 2 |
| nvoPM-F_DmndCh14 | SNVT_count_f | Demand Channel 14 | Pulse | R | 2 |
| nvoPM-F_DmndCh15 | SNVT_count_f | Demand Channel 15 | Pulse | R | 2 |
| nvoPM-F_DmndCh16 | SNVT_count_f | Demand Channel 16 | Pulse | R | 2 |
| nvoRTC_DateTime | SNVT_time_stamp | Time | Time | R |  |
| nvoRTC_DayofWeek | SNVT_date_day | Date | Date | R |  |

- Can only clear using ModBus RTU.  Jumper J7 must be closed.  LonWorks module must be removed to access ModBus RTU.

- Can only clear using ModBus RTU.  Jumper J7 must be closed.  LonWorks module must be removed to access ModBus RTU.

E-Mon D-Mon BACNET

- PIC STATEMENT for Class 3200, 3400, 5000 Meters & IDRs

BACNET PROTOCOL IMPLEMENTATION CONFORMANCE STATEMENT

Date: 	August 2011

Vendor Name: 	E-Mon

Vendor ID:	482

Product Name: 	Class 3200 Meter, Class 3400 Meter, Class 5000 Meter, IDR

Product Model Numbers:	E32-208100-RBACKIT, E34-480200-R05KIT, E50-480200-R03KIT, EIDR-8-R05RJ

Product Description:	This product will provide bi-directional communication between E-Mon BACnet MS/TP meters, BACnet IP meters, and a BACnet system.

BACnet Standarized Device Profile (Annex L):

 	BACnet Smart Sensor (B-SS)

BACnet Interoperability Building Blocks Supported (Annex K):

 	K.1.2 BIBB - Data Sharing - ReadProperty-B (DS-RP-B)

 	K.1.4 BIBB - Data Sharing - ReadPropertyMultiple-B (DS-RPM-B)

 	K.5.2 BIBB - Device Management - Dynamic Device Binding-B (DM-DDB-B)

 	K.5.4 BIBB - Device Management - Dynamic Object Binding-B (DM-DOB-B)

Segmentation Capability:

None

Standard Object Types Supported:

 	Device Object

 	Analog Input

For all these properties the following apply:

1. 	Does not support BACnet CreateObject

2. 	Does not support BACnet DeleteObject

3. 	No additional writeable properties exist

4. 	No proprietary properties exist

5. 	No range restrictions exist

Data Link Layer Options:

 	MS/TP master (Clause 9), baud rate(s): 9.6k, 19.2k, 38.4k, 76.8k bps

 	BACnet IP, (Annex J): Class 3200 meter does not support BACnet IP

Device Address Binding:

Not supported

Character Sets Supported:

 	ANSI X3.4